The following questions can be used to help evaluate whether existing eyewash stations are adequate. This information was obtained from OPN 143, Appendix A.

General Questions - Ask the employee what they will do if they get a chemical in their eyes or on their face or skin. - Ask the employee if the employer has informed them what to do if there is a chemical splash to their eyes, face or skin. - Ask the employee where the eye and face wash and shower facilities they are expected to use are located. - Ask where other nearby water sources are located. - Ask the employer what assessments were made to determine if eye and face wash or showers are necessary. - Ask the employer what things were considered in determining the adequacy of the facility.

Accessibility - Location, Activation and Availability of Facility at Time Needed - What is the distance to the closest facility? (Measure it if possible.) ___________ - How long does it take to walk at a normal pace to the closest facility? (Walk the length.) _________________ - Is the room where the facility is located locked or can it be locked at the time it is needed (such as a bathroom or closet)? - How long does it take for an employee to turn the facility on? (Have someone demonstrate.) - Does the facility remain on after it is turned on? - If the facility does not remain on, what must the injured employee do to keep the water flowing? (Have someone demonstrate.) - If using a facility that has other intended use (such as a kitchen sink, shower or hose), is the facility available when needed? (e.g. is the hose in use somewhere else at the time it might be needed for rinsing the eyes such that the injured employee cannot use it? Is the sink full of dishes at a time that an employee might need it to rinse such that it is not able to be used as eyewash?) - Is the facility located in a relatively direct path from the hazard so that the employee can reach it without circumventing moving machinery or other dangerous equipment, use stairs or open doors? (Walk the path of the closest facilities, take photos of obstructions.) - Do employees work alone?

Water Spray Pattern, Volume, Temperature & Pressure - Is the spray pattern appropriate for the expected use of the facility and hazards present? - Is water pressure high enough that the water reaches the employee’s eyes or face? - Is the water pressure so high that it could cause eye injury or prevent the employee from keeping their face or body in the water stream? - Is the volume of water available sufficient to flush the face or body for 15 minutes? - Is the temperature mild enough that an employee will keep their face in the water stream and not suffer hypothermia or burn their skin? (Temperatures between 60 & 90 degrees are ideal and recommended by ANSI.) - Is hot water connected to the facility? - Can hot water only be turned on due the faucet type? - What is the temperature of the water? - Is there a temperature regulator?