Electrical Safety 

Purpose

The purpose of the Electrical Safety program is to set forth procedures for the safe use of electrical equipment, tools, and appliances at COMPANY..

Scope

This program applies to all COMPANY. employees, temporary employees, and contractors. When work is performed on a non-owned or operated site, the operator’s program shall take precedence, however, this document covers COMPANY. employees and contractors and shall be used on owned premises, or when an operator’s program doesn’t exist or is less stringent.

Definitions

Affected Personnel - Personnel who normally use and work with electrical equipment, tools, and appliances, but who do not make repairs or perform lock out/tag out procedures. 

Appliances - Electrical devices not normally associated with commercial or industrial equipment such as air conditioners, computers, printers, copiers, coffee pots, microwave ovens, toasters, etc. 

Circuit Breaker - A device designed to open and close a circuit by non-automatic means and to open the circuit automatically on a predetermined over current without injury to itself when properly applied within its rating. 

Disconnecting Means - A device, or group of devices, or other means by which the conductors of a circuit can be disconnected from their source of supply. 

Disconnecting Switch - A mechanical switching device used for isolating a circuit or equipment from a source of power.  

Double Insulated Tool - Tools designed of non-conductive materials that do not require a grounded, three wire plug. 

Ground - Connected to earth or some conducting body that serves in place of the earth.  

Grounded Conductor - A conductor used to connect equipment or the grounded circuit of a wiring system to a grounding electrode or electrodes. 

Ground Fault Circuit Interrupter (GFCI) - A device whose function is to interrupt the electric circuit to the load when a fault current to ground exceeds some predetermined value that is less than that required to operate the over current protective device of the supply circuit. 

Insulated - A conductor encased within material of composition and thickness that is recognized as electrical insulation.  

Premises Wiring - That interior and exterior wiring, including power, lighting, control, and signal circuit wiring together with all of its associated hardware, fittings, and wiring devices, both permanently and temporarily installed, which extends from the load end of the service drop, or load end of the service lateral conductors to the outlet (s). Such wiring does not include wiring internal to appliances, fixtures, motors, controllers, motor control centers, and similar equipment. 

Electrical Safety 

Qualified Person - One that has been trained in the repair, construction and operation of electrical equipment and the hazards involved.  

Strain Relief - A mechanical device that prevents force from being transmitted to the connections or terminals of a cable or extension cord. 

Class l Locations - Are those in which flammable gases or vapors are or may be present in the air in quantities sufficient to produce explosive or ignitable mixtures. 

Class 1 Division 1 - Is a location (a) in which hazardous concentrations of flammable gases or vapors may exist under normal operating conditions; or (b) in which hazardous concentrations of such gases or vapors may exist frequently because of repairs or maintenance operations or because of leakage; or (c) in which a breakdown or faulty operation or equipment or processes might release hazardous concentrations of flammable gases or vapors, and might also cause simultaneous failure of electrical equipment. 

Class 1 Division 2 - Is a location (a) in which volatile flammable liquids or flammable gases are handled, processed, or used, but in which the hazardous liquid, vapors, or gases will normally be confined within closed containers or closed systems from which they can escape  only in case of accidental rupture or breakdown of such containers or systems, or in of abnormal operation of equipment or (b) in which hazardous concentrations of gases or vapors are normally prevented by positive  mechanical ventilation, and which might become hazardous through failure or abnormal operations of the ventilating equipment; or (c) that is adjacent to a Class 1, Division 1 location, and to which hazardous concentrations of gases or vapors might occasionally be communicated unless such communication is prevented by adequate positive-pressure  ventilation from a source of clean air, and effective safeguards against ventilation failure are provided. 

Class II locations - Class II locations are those that are hazardous because of the presence of combustible dust.  Class II locations include the following:  

Class II, Division 1 - A Class II, Division 1 location is a location (a) in which combustible dust is or may be in suspension in the air under normal operating conditions, in quantities sufficient to produce explosive or ignitable mixtures; or (b) where mechanical failure or abnormal operation of machinery or equipment might cause such explosive or ignitable mixtures to be produced, and might also provide a source of ignition through simultaneous failure of electric equipment, operation of protection devices, or from other causes, or (c) in which combustible dusts of an electrically conductive nature may be present. 

NOTE: This classification may include areas of, areas where metal dusts and powders are produced or processed, and other similar locations that contain dust producing machinery and equipment (except where the equipment is dust-tight or vented to the outside).   

· These areas would have combustible dust in the air, under normal operating conditions, in quantities sufficient to produce explosive or ignitable mixtures. 

· Combustible dusts that are electrically nonconductive include dusts produced in the handling and processing produce combustible dusts when processed or handled. 

· Dusts containing magnesium or aluminum are particularly hazardous and the use of extreme caution is necessary to avoid ignition and explosion. 

Electrical Safety 

Class II, Division 2 - A Class II, Division 2 location is a location in which:  (a) combustible dust will not normally be in  suspension in the air in quantities sufficient to produce explosive or ignitable mixtures, and dust accumulations are normally insufficient to interfere with the normal operation of electrical equipment or other apparatus; or (b) dust may be in suspension in the air as a result of infrequent malfunctioning of handling or processing equipment, and dust accumulations resulting there from may be ignitable by abnormal operation or failure of electrical equipment or other apparatus. 

NOTE: This classification includes locations where dangerous concentrations of suspended dust would not be likely but where dust accumulations might form on or in the vicinity of electric equipment. These areas may contain equipment from which appreciable quantities of dust would escape under abnormal operating conditions or be adjacent to a Class II Division 1 location, as described above, into which an explosive or ignitable concentration of dust may be put into suspension under abnormal operating conditions.  

Responsibilities

Managers/Supervisor

The Safety Director will develop electrical safety programs and procedures in accordance with OSHA requirements and/or as indicated by events and circumstances.  

Operations Managers and Supervisors are responsible for ensuring that only qualified employees and or qualified contractors perform electrical repairs or installations. 

Operations Managers are also responsible for ensuring all applicable electrical safety programs are implemented and maintained at their locations.  

Employees are responsible to use electrical equipment, tools, and appliances according to this program, for attending required training sessions when directed to do so and to report unsafe conditions to their supervisor immediately. 

Only qualified employees may work on electric circuit parts or equipment that has not been de-energized.  Such employees shall be made familiar with the use of special precautionary techniques, PPE, insulating and shielding materials and insulated tools. 

Electrical Safety 

Safe Work Practices

Inspections

· Electrical equipment, tools, and appliances must be inspected prior to each use. 

· The use of a hard fixed GFCI or a portable GFCI adapter shall be used with all portable hand tools, electric extension cords, drop lights and all 110 volt equipment. 

· Faulty equipment, tools, or appliances shall be removed from service immediately and tagged “Out of Service”, dated and signed by the employee applying the tag. 

Repairs

· Only Qualified Personnel, who have been authorized by the department supervisor or manager, may make repairs to supply cords on electrical tools and to extension cords. 

· The names of employees authorized to make repairs will be posted in the workplace.  

· Only certified electricians shall be allowed to make repairs to electrical equipment and wiring systems. 

· The supervisor obtaining the services of a certified electrician is responsible to verify the electrician’s credentials.  

· Employees shall not enter spaces containing exposed energized parts unless qualified and proper illumination exists to enable employees to work safely. 

· Employees shall not wear conductive apparel such as rings, watches, jewelry, etc. (unless they are rendered non-conductive by covering, wrapping, or other insulating means) while working on or near open energized equipment this includes batteries on trucks, forklifts, phone backup systems or other such equipment. 

· If employees are subject to handle long dimensional conductor objects (ducts or pipes), steps for safe work practices shall be employed to ensure the safety of workers.

Extension Cords

· Use only three-wire, grounded, extension cords and cables that conform to a hard service rating of 14 amperes or higher, and grounding of the tools or equipment being supplied. 

· Only commercial or industrial rated-grounded extension cords may be used in shops and outdoors.  

· Cords for use other than indoor appliances must have a rating of at least 14 amps. 

· Cords must have suitable strain relief provisions at both the plug the receptacle ends. 

· Work lamps (drop light) used to power electrical tools must have a 3 wire, grounded outlet, unless powering insulated tools.  

· Adapters that allow three wire, grounded prongs, connected to two wire non-grounded outlets are strictly prohibited. 

· Cords must have a service rating for hard or extra-hard service and have S, AJ, ST, SO, SJO, SJT, STO, or SJTO printed on the cord.  

· Cords may not be run through doorways, under mats or carpets, across walkways or aisles, concealed behind walls, ceilings or floors, or run through holes in walls, or anywhere where they can become a tripping hazard. 

· High current equipment or appliances should be plugged directly into a wall outlet whenever possible.  

· All extension cords shall be plugged into one of the following:  

· A GFCI outlet;  

· A GFCI built into the cord; 

· A GFCI adapter used between the wall outlet and cord plug.  

Electrical Safety 

· All extension cords and or electrical cords shall be inspected daily or before each use, for breaks, plug condition and ground lugs, possible internal breaks, and any other damage. If damage is found, the extension cord or electrical cord shall be remove from service and repaired or replaced. 

· Extension cords shall not be used on compressor skid to operated heat tapes or any other type of equipment on a temporary basis. Heat tapes or other equipment shall be hard wired per applicable electrical codes.

Outlets

· Outlets connected to circuits with different voltages must use a design such that the attachment plugs on the circuits are not interchangeable. 

Multiple Outlet Boxes

· Multiple outlet boxes must be plugged into a wall receptacle. 

· Multiple outlet boxes must not be used to provide power to microwave ovens, toasters, space heaters, hot plates, coffeepots, or other high-current loads. 

Double Insulated Tools

· Double insulated tools must have the factory label intact indicating the tool has been approved to be used without a three wire grounded supply cord connection. 

· Double insulated tools must not be altered in any way, which would negate the factory rating.  

Switches, circuit breakers, and disconnects

· All electrical equipment and tools must have an on and off switch and may not be turned on or off by plugging or unplugging the supply cord at the power outlet. 

· Circuit breaker panel boxes and disconnects must be labelled with the voltage rating.  

· Each breaker within a breaker panel must be labelled for the service it provides. 

· Disconnect switches providing power for individual equipment must be labelled accordingly.  

Ladders

· Only approved, non-conductive ladders, may be used when working near or with electrical equipment, which includes changing light bulbs. 

· Ladders must be either constructed of wood, fiberglass, or have non-conductive side rails.  

· Wood ladders should not be painted, which can hide defects, except with clear lacquer. 

· When using ladders they shall be free from any moisture, oils, and greases. 

Energized and Overhead High Voltage Power Lines & Equipment 

· A minimum clearance of 10 feet from high voltage lines must be maintained when operating vehicular and mechanical equipment such as forklifts, cranes, winch trucks, and other similar equipment. 

· When possible, power lines shall be de-energized and grounded or other protective measures shall be provided before work is started. 

· Minimum approach distance to energized high power voltages lines for unqualified employees is 10 feet.  

· Minimum approach distance for qualified employees shall be followed per 29 CFR 1910.333(c)(3)(i) Qualified – Table S5 Selection and Use of Work Practices -  Approach Distances for Qualified Employees – Alternating Current).  

Electrical Safety 

Confined or Enclosed Work Spaces

· When an employee works in a confined or enclosed space that contains exposed energized parts, the employee shall isolate the energy source and turn off the source and lock and tag out the energy source (Only qualified electricians can work on an exposed energy source). 

· Protective shields, protective barriers or insulating materials as necessary shall be provided.  

Enclosures, Breaker Panels, and Distribution Rooms  

· A clear working space must be maintained in the front, back and on each side of all electrical enclosures and around electrical equipment for a safe operation and to permit access for maintenance and alteration. 

· A minimum two-foot working floor space in front of panels and enclosures shall be painted yellow.  

· Employees may not enter spaces containing exposed energized parts unless illumination is provided that enables the employees to work safely.  

· Housekeeping in distribution rooms must receive high priority to provide a safe working and walking area in front of panels and to keep combustible materials to the minimum required to perform maintenance operations. 

· All enclosures and distribution rooms must have “Danger: High Voltage – Authorized Personnel Only” posted on the front panel and on entrance doors. 

· Flammable materials are strictly prohibited inside distribution rooms (Boxes, rags, cleaning fluids, etc.)  

Lock Out/Tag Out

· No work shall be performed on (or near enough to them for employees to be exposed due to the dangers of tools or other equipment coming into contact with the live parts) live parts and the hazards they present.

· If any employee is exposed to contact with parts of fixed electric equipment or circuits which have been de-energized, the circuits energizing the parts shall be locked out or tagged or both.

· Conductors and parts of electrical equipment that have been de-energized but not been locked or tagged out shall be treated as live parts.  

· Per COMPANY. policy all electrical will be outsourced and performed only by qualified and licensed electrical contractors who are familiar with the use of special precautionary techniques, PPE, insulating and shielding materials and insulated tools.  Any equipment being made ready for maintenance will be locked out using COMPANY.’s Control of Hazardous Energy – Lock Out/Tag Out Program. Lockouts are performed by the Safety Director, Shop Foreman or Branch Manager. Designated employees in some branches may be trained by local management to lock out equipment.  If live sources are to be worked it will only be performed with the knowledge of local management.  Only certified electricians may work on electric circuit parts or equipment.

· Only authorized personnel may perform lock out/tag out work on electrical equipment and will follow COMPANY.’s Control of Hazardous Energy – Lock out/Tag Out Program. 

· Authorized personnel will be trained in lock out/tag out procedures. 

· Affected personnel will be notified when lock out/tag out activities are being performed in their work area. 

Electrical Safety 

Contractors

· Only approved, certified, electrical contractors may perform construction and service work on COMPANY. or client property. 

· It is the Manager/Supervisors responsibility to verify the contractor’s certification.  

Fire Extinguishers

· Approved fire extinguishers must be provided near electrical breaker panels and distribution centers.  

· Water type extinguishers shall not be located closer than 50 feet from electrical equipment. 

Electric Shock-CPR: 

· If someone is discovered that has received an electric shock and is unconscious, first check to see if their body is in contact with an electrical circuit. Do not touch a person until you are sure there is no contact with an electrical circuit. 

· When it is safe to make contact with the victim, begin CPR if the person’s heart has stopped or they are not breathing.  

· Call for help immediately.  

Electric Welders

· A disconnecting means shall be provided in the supply circuit for each motor-generator arc welder, and for each AC transformer and DC rectifier arc welder which is not equipped with a disconnect mounted as an integral part of the welder. 

· A switch or circuit breaker shall be provided by which each resistance welder and its control equipment can be isolated from the supply circuit. The ampere rating of this disconnecting means may not be less than the supply conductor ampacity. 

Equipment Grounding

· All gas compressors, air compressors, separators, vessels, etc. shall be grounded by means of using a lug and ground strap, nominal in size to a ½” bolt or larger, attached to a ground rod six feet or longer. 

· Equipment bonding jumpers shall be of copper or other corrosion-resistance material.  

· The transfer of hazardous or flammable material from a metal or plastic container with a flash point of 100 degrees F or less shall have a ground strap from the container and attached to the skid or a ground rod placed in the ground. 
Electrical Safety 

Training

All regular full time and temporary employees will be trained in Electrical Safety utilizing the COMPANY. Electrical Safety Training course or an approved equivalent. 

Employees who face a risk of electric shock, but who are not qualified persons, shall be trained and familiar with electrically related safety practices. 

Employee shall be trained in safety related work practices that pertain to their respective job assignments.  

Employees shall be trained on clearance distances.  

Safe work practices shall be employed to prevent electric shock or other injuries resulting for either direct or indirect electrical contacts when work is performed near or on equipment or circuits which are or may be energized. 

Electrical Safety – Overhead Distribution & Transmission

Electrical equipment and lines shall always be considered as energized unless they are positively

proven to be de-energized and properly grounded. IF IT ISN'T GROUNDED - IT ISN'T

DEAD!

· Only authorized employees shall work on or near energized lines or equipment.

· No employee shall approach any exposed ungrounded line wire or apparatus unless he is insulated from other conducting surfaces or uses adequate protective devices.

· Employees shall report immediately to their nearest foreman or supervision any defective Line, apparatus or tool or other condition which in their judgment may be dangerous either to persons or property or likely to interrupt or delay service.

· Electrical equipment and tines shall always be considered as "live" unless they are positively known to be dead and grounded. 
· Before starting to work, preliminary inspection or test shall be made to determine what conditions exist. Extreme care shall be exercised when handling common neutral conductors as high voltage may be encountered.

· Secondary windings of current or series transformers shall be short circuited before any instrument or other device connected in the circuit is removed or disconnected.

· A thorough understanding of the work to be. Performed shall be communicated through tailgate conferences or safety meetings conducted by the supervisor prior to beginning work.

· While working on a pole with wires or lines, workmen shall work below the lines. He should use caution and only do one task at a time.

· Metal objects such as keys, rings, watch linemen shall not wear chains, badges, or necklaces as they can possibly increase the hazard of electrical contact.

· Hot line sticks are required when opening, closing, installing, or removing switch barrels.

· Never use your hands!
· Confined space entry procedures shall be in full force whenever work is to be done in manhole or vault. The supervisor shall positively identify the cable.
· Before cutting the insulation on a cable in a vault or manhole an electric test shall be made where the work is to be done.

· Work areas shall be roped off, marked and identified to prevent accidental entry into dangerous areas. Flares, flashing lanterns, and signs shall be used to identify and protect the work area.
Flexible Protective Equipment (Rubber or Synthetic)

· Employees shall not touch or work on any exposed energized lines or apparatus except when wearing protective equipment approved for the voltage to be contacted.

· When work is to be done on or near energized lines or equipment, all energized and grounded conductors, of any part of the body shall be- covered with protective equipment, except that part of the conductor on which the employee is working.

· When working on energized lines or apparatus, including the installation of protective devices, work should be done from below, if possible.

· In applying flexible protective equipment, an employee shall always protect the nearest and lowest wires first, protecting himself as he progresses. In removing rubber protective equipment, the reverse order shall be maintained.

· Flexible blankets shall not be used on the ground without protecting them from physical damage and moisture by means of a tarpaulin, canvas, or protective mat.

· Protective equipment shall be put on or before entering the working area within which energized lines or apparatus may be reached, and the protective equipment shall not be removed until the employee is completely out of reach of this area.

· To avoid corona and ozone damage, rubber protective equipment shall not be allowed to remain in place on energized lines or apparatus overnight or for more than one eight-how period, unless approved by the supervisor in charge.

Electrical Safety – Overhead Distribution & Transmission

Flexible Protective Equipment (Rubber or Synthetic)

· Line hose, hoods, blankets, line guards, etc, shall be visually inspected before each job.

· Flexible protective devices shall be stored in special compartments on trucks and elsewhere where they will not be subjected to damage from tools or other equipment.

· Bare communications conductors shall be treated as energized lines and shall be protected accordingly.
Use and Care of Rubber Gloves

· Only authorized employees or those under the continuous supervision of an experienced Workmen shall wear rubber gloves, with leather protectors, when working on lines or equipment energized at voltages above 110 volt*, unless hot-line tools are used.
· When the use of rubber gloves is required, they will be put on while in the ground position and kept on until the lineman returns to the ground position.

· Rubber gloves with leather protectors shall be worn when;
· Working on any structure upon which is mounted it any position, an energized conductor (to include de-energized but ungrounded conductors which are to be Working on or within falling or reaching distance of any electrical equipment or metal-surfaces {cross arms, cross-arm braces or transformer cases) which are not effectively grounded and which may be or may become energized above 110 volts to ground;

· During wet or stormy weather, working on or within falling or reaching distance of any conductor or equipment which may be or may become energized at any voltage;
· Required by supervision;

· Removing lead sheath and sleeves from cables and joints, and opening or cutting cables (until they have been proven to be de-energized at the work location by positive tests);

· Making statiscope tests on cable;

· Operating manually controlled air break switches (unless protected by a grounding mat or grid);

· Opening and closing manually operated air circuit breakers

· Making tests to determine if lines are de-energized, and applying and removing grounding devices;
· Working on or near series street lighting circuits even though they are disconnected from the source of power;

· Repairing series fixtures or attachments, the circuit of which is exposed to 'energized conductors, except where the fixtures are disconnected from the line;

· Pulling in wires or handling other conducting materials near circuits, apparatus or equipment which is, or may become energized;

· Working on or near telephone or other circuits which are subject to induced voltages from energized high voltage circuits, innless such circuits to be worked are adequately grounded;

Electrical Safety – Overhead Distribution & Transmission

· When rubber glove work is authorized to be performed on circuits from 5 kV to 15 kV, gloves rated at 20,000 volts shall be used. For circuits above 15 kV, gloves rated at 30,000 volts shall be used.

· When working with rubber protective equipment on energized circuits or apparatus where the voltage between any two conductors is over 7,500 volts, the following minimum conditions shall be met in addition to all other rules governing the use of protective equipment:

· Rubber gloves shall be used;

· Employee shall not make physical contact with protective devices installed on energized primary conductors with other than his rubber gloves or rubber sleeves;

· Employee shall be isolated from all grounds (wooden poles shall be considered as grounds in this case) by using approved supplementary insulation such as aerial baskets, a lineman's platform, or other approved insulated devices.

· Rubber gloves shall never be worn inside out or without leather protectors, they shall be exchanged at any time they become damaged or the employee to when they are assigned becomes suspicious of them. Leather protectors or overgloves shall not be worn except when in use over rubber gloves.

· Rubber gloves shall be inspected for corona cracks or other damage and shall be given air test at least once each day while in use, preferably at the beginning of the work period and at any other time when their condition is in doubt. They shall be checked before each use.

· Gloves when not in use shall be kept in canvas bags or other approved containers and stored where they will not become damaged by sharp objects or exposed to direct sunlight. They shall never be folded while stored or shall other objects be placed upon them.

· Rubber gloves shall be stored in the glove bag with the cuffs down to permit drainage, better ventilation and reduce the possibility of damage.

· Rubber gloves shall be changed out and tested every six months. The supervisor will be responsible for changing out the gloves on his crew. Spare gloves are kept at the Company office in Meridian, Mississippi.
Electrical Safety – Overhead Distribution & Transmission

Climbing or Working on Poles

· All poles and structures shall be carefully inspected before climbing to assure that they are in a safe condition for the work to be performed and that they are capable of sustaining the additional or unbalanced phases to which they will be subjected.

· Where poles or structures may be unsafe for climbing, they shall not be climbed until made safe by guying, bracing, or by other adequate means

· Wires shall not be attached to or removed from a pole or structure until it is certain that the pole or structure will withstand the altered strain.

· Poles, except new poles, shall be thoroughly. Tested before they are climbed. If a pole is not strong enough to sustain a lineman's weight by reason of its condition or its placement (such as in soft ground); it shall be guyed or otherwise secured throughout the time any work is being performed on it If the pole to be climbed is being replaced and the new pole is set adjacent to it, the old pole may be lashed to the new one in lieu bf guying,

· When poles are encountered which are unsafe to climb (ice, badly chewed, wide cracks, shell rot, etc.) an alternate means of climbing shall be used (use belt around pole white climbing) or the use of an aerial basket shall be considered.

· Workmen shall not wear their climbers while driving or riding in vehicles or when doing work on the ground, on ladders (except hook ladders) or on platforms in which the' wearing of the climbers creates a hazard.

· Gaffs on climbers shall be kept within safe length limits (1-1/4  inches min.), properly shaped, and sharp.

· Employees shall not work on an elevated pole or structure without first securing themselves with a safety strap.

· Only approved belts and straps shall be used.

· Metal hooks, chains, etc., for holding tools or tape shall not be attached to body belts.

· Leather or other non-conducting material shall be used for this purpose.
· The safety strap shall not be put around a pole above the uppermost pole attachment position, except where pole top or attachment is above eye level. It shall not be used on pole steps, crossarm braces, insulators, insulator pins, conductors, rotten or otherwise weak cross arms or on attachments that are being moved. When it is necessary to attach to a cross arm, the safety strap shall never be placed beyond the outside cross arm attachment.

· It shall be so placed that it will not be cut by line equipment or twisted or fouled by material that may give way under strain
· Employees shall not trust their weight to guy wires; pins, braces, conductors or other such equipment that might prove unstable.

· When two or more employees are to work on the same pole at the same time, each shall reach the working position before the next leaves the ground, They shall descend the pole one at a time.
· When climbers are stored in the truck or tool room they shall be placed where the sharp points will not damage other equipment or cause personal injury.

Electrical Safety – Overhead Distribution & Transmission

Working on Energized Lines with Live Line Tools

· Lines of #6 copper, #6 ACSR, and #8A copper weld or smaller shall not be worked on with live-line tools except in specific instances where continuity in Service is vital and then only upon special authorization.

· Planned work with live-line tools shall not be started during unfavorable weather.

· Before work with live-line maintenance tools is begun, the dispatcher or person having jurisdiction shall be notified. If during live-line tool work, an interruption of service occurs, the dispatcher or other person having jurisdiction shall be notified immediately.

· Only tools approved by the Company shall be used in live-line maintenance work.

· A careful check shall be made to see that the condition of the structure and lines at the point of the work is such that the job may be performed safely. In addition the adjacent spans and structures shall be carefully checked for defects in conductors, tie wires, insulators, and other equipment

· Under no circumstances shall a lineman depend on another lineman to hold a conductor clear of him.

· Positive care shall be maintained during the movement of any conductor.  
· Live-Line work is in progress, no other work*. of any nature shall be performed on the same pole or structure.
· AII live-line tools, when not in use, shall be kept in canvas bags or weatherproof boxes provided for that purpose.  These containers shall be stored in a dry shed, if possible in a warm place.
· Live-line tools shall never be laid directly on the ground or against sharp objects such as barbed wire fences.  Special tool holders or tarps shall be used for this purpose.
· All live line tools hilt be visually inspected before use each day. Tools to be used shall be wiped clean and if any hazardous defects are indicated, these tools shall be removed from service.

· When practical, the automatic re-closing feature of circuit interrupting devices shall be made inoperative before work begins.
:

